## Slide 1: Municipal Utilities & Engineering Department
Status of the City of Redlands Wastewater Treatment Plant (WWTP)

## Slide 2: Discussion
History of WWTP
Current Operations Status
Condition Assessment
WWTP Options
Next Steps

## Slide 3
WWTP – Present day
Notes: - Current site east of California Street Landfill and south of Santa Ana River

## Slide 4
1962 - Original WWTP constructed
Secondary Treatment
Primary Clarifiers
Primary & Secondary Digester
Capacity of 5.0 MGD
Discharge to Santa Ana River
Inlet Structure
Sludge Beds
Notes: - Capacity of 5 MGD and discharging to Santa Ana River

## Slide 5
Storage Pond
Sludge Beds
Headworks
Primary Clarifier
Trickling Filter
Aeration Basins
Secondary Clarifier
Primary Digester & Sludge Thickening
Capacity of 6.0 MGD
Discharge to Percolation Ponds east of Alabama
1972 – Expansion & modification
Notes: Clean Water Act 1972 led to increased discharge requirements
6 MGD and discharging to spreading grounds

## Slide 6
Primary Clarifier
Storage Pond
TF Clarifier
Secondary Clarifier
Primary Digester
Sludge Beds
Capacity of 9.0 MGD
1987 – 1989 Expansions for growth
Admin. Bldg.
Notes: - Numerous expansions for growth between 1987 and 1989

## Slide 7
Membrane Bioreactor
Chlorine Contact Tank
Aeration Basin Modification
Capacity of 9.5 MGD
6.0 MGD recycled water
3.5 MGD conventional
2004 – Recycled water system
Notes: Effort to produce recycled water in response to drought conditions
Produce recycled water for Mountain View Power Plant
Engine and transmission analogy

## Slide 8
WWTP – Current facility status
Notes: Trickling filter from 1972 and secondary clarifier from 1988 out of service due to evolving technology and reduced flows to conventional treatment side
Current plant is a composition of 57 years of infrastructure

## Slide 9: Current Operations Status
Current average flows of 5.5 MGD
  Flows are split between MBR (recycled water) and conventional (treated water to be recharged)
Current permitted capacity projected to be adequate until at least 2040, based upon anticipated growth and continued conservation

## Slide 10: Operations Challenges
Membrane Bioreactor (MBR)
  MBR completed in 2004
  Typical lifespan = 8 years
Notes: Large amount of buildup due to lack of fine screens
Strands falling out of module
Engine of the car

## Slide 11: Operations Challenges
Aeration Basins
  Constructed in 1972, modified in 2004
  Cannot isolate basins or maintain air diffusers
Notes: - Transmission of the car

## Slide 12: Operations Challenges
Electrical Infrastructure
  Aging electrical system, some equipment from 1962
  Critical electrical service infrastructure installed in 1972
  Update to current code requirements
1962 Motor Control Center
1972 Switchboard

## Slide 13: Operations Challenges
Supervisory Control and Data Acquisition
  Many of the WWTP key processes are not connected to the SCADA system and are controlled manually

## Slide 14: Operations Challenges
Efficiency
  Energy
  Limited operational flexibility to treat evolving incoming flow
      Water conservation
      Industry discharge
  Technology improvements to increase treatment efficiency
Reliability
  Provide redundancy of critical processes
  Limited parts for repairs leading to abandonment or increased costs and delay for repair

## Slide 15: Operations Challenges
Additional challenges:
  Evaluate in kind replacement for MBR
  Constant reactive state from operations staff
  Difficult to maintain regulatory compliance with potential failures of critical infrastructure
  Pending implementation of best management practices from regulatory agencies
  Potential to impede future economic development
Notes: - In order to continue operations or current WWTP

## Slide 16: Condition Assessment
How do we address the challenges?
Request for Proposals (RFP) in early 2018
Purpose:
  Independent assessment of facilities
  Roadmap for future

## Slide 17: RFP Scope
Task 1 – Field Assessment
Task 2 – Project Report/Implementation Plan
Task 3 – Engineering Design Services
Task 4 – Construction Management Services

## Slide 18: RFP Outreach
Outreach effort
Pre-proposal conference
  12 engineering consultants attended
  2 hour tour and visual assessment
Follow-up visits
  Staff provided 6 independent tours
  Over 200 hours spent assessing plant

## Slide 19: RFP Process
Received 4 proposals
Evaluation Process
  Reviewed proposals
  Completed interviews
Developed scope of work based on:
  Visual Assessment;
  Standard industry practices;
  Recommendation of engineering professionals; and
  Discussion with field operations staff.

## Slide 20: Options for WWTP
Rehabilitation of existing WWTP
  Phased improvements
  Comprehensive improvements
Construction of a new WWTP

## Slide 21: Rehabilitation of existing WWTP
Membrane Bioreactor System
  Install MBR system
  Install fine screens
  Replace/upgrade piping and back wash system
Aeration Basins
  Modification and rehabilitation
  Install high speed turbo blowers
  Replace piping, valves and other appurtenances
  Headworks Upgrades
  Washer/compactor for screenings and grit
Solids Handling System Upgrades
Miscellaneous Facility Improvements
Improvement life of 20-25 years
  Note: Electrical, control & site improvements included within each item above.
Notes: Recommended rehabilitation items identified through assessment process

## Slide 22: Phased Improvement Projects
Total cost (Phase 1 & 2) = $43.8 Million
Phase 1 (2-3 years) total cost = $32.8 Million
  Design = $2.8 Million
  Construction = $30 Million
    Membrane Bioreactor System (MBR) = $12.6 Million
    Aeration Basins = $14.7 Million
    10% Contingency = $2.7 Million
    Phase 2 (7-8 years) total cost = $11 Million
  Construction = $11 Million
    Headworks = $6.3 Million
    Solids Handling System = $2.5 Million
    Additional Facility Improvements = $1.2 Million
    10% Contingency = $1 Million
Notes: Implement recommended improvements in a phased approach with Phase 1 in 2-3 years and Phase 2 in the future, potentially 7-8 years for completion.

## Slide 23: Comprehensive Improvement Project
Total cost = $41.3 Million
  Design = $2.8 Million
  Construction = $38.5 Million
    Membrane Bioreactor System (MBR) = $12.6 Million
    Aeration Basins = $14.7 Million
    Headworks = $4.7 Million
    Solids Handling System Upgrades = $2 Million
    Additional Facility Improvements = $1 Million
    10% Contingency = $3.5 Million
    Same design and construction scope as phased improvement project but completed in 2-3 years instead of 7-8 years
Notes: Implement same construction scope as phased approach but in a 2-3 timeframe
Same design scope for a phased or comprehensive approach

## Slide 24: Construction of a new WWTP
Total cost = $100 Million
  Design = $8 Million
  Construction = $92 Million ($84 Million + 10% Contingency)
New treatment facilities adjacent to existing WWTP with same capacity
Improvement life of 30-35 years
Anticipate completion timeline of 4-6 years
Notes: - Cost based on recently awarded WWTP in Highland and Beaumont

## Slide 25: Summary
 | Cost ($ Million) | Project Time (years) | Lifespan (years)
Phased | $43.8 | 7-8 | 20-25
Comprehensive | $41.3 | 2-3 | 20-25
New | $100 | 4-6 | 30-35

## Slide 26: Next Steps
Award design contract
Conduct Peer Evaluation
Engage services of financial consultant to develop a revenue program and explore potential financing options
Solicit applications for formation of Utilities Advisory Committee (UAC)
Notes: Scope developed to complete either a phased or comprehensive rehabilitation project
Construction phasing can be decided during detailed design and once financial analysis is completed

## Slide 27: Questions